BSR/ASHRAE Addendum o

to ANSI/ASHRAE Standard 34-2024

First Public Review Draft

Proposed Addendum o to

Standard 34-2024, Designation and Safety Classifications of Refrigerants

First Public Review (April 2026)

(Draft shows Proposed Changes to Current Standard)

This draft has been recommended for public review by the responsible project committee. To submit a comment on this proposed standard, go to the ASHRAE website at https://www.ashrae.org/technical-resources/standards-and-guidelines/public-review-drafts and access the online comment database. The draft is subject to modification until it is approved for publication by the Board of Directors and ANSI. Until this time, the current edition of the standard (as modified by any published addenda on the ASHRAE website) remains in effect. The current edition of any standard may be purchased from the ASHRAE Online Store at www.ashrae.org/bookstore or by calling 404-636-8400 or 1-800-727-4723 (for orders in the U.S. or Canada).

This standard is under continuous maintenance. To propose a change to the current standard, use the change submittal form available on the ASHRAE website, www.ashrae.org.

The appearance of any technical data or editorial material in this public review document does not constitute endorsement, warranty, or guaranty by ASHRAE of any product, service, process, procedure, or design, and ASHRAE expressly disclaims such.

© 2026 ASHRAE. This draft is covered under ASHRAE copyright. Permission to reproduce or redistribute all or any part of this document must be obtained from the ASHRAE Manager of Standards, 180 Technology Parkway NW, Peachtree Corners, GA 30092. Phone: 404-636-8400, Ext. 1125. Fax: 404-321-5478. E-mail: standards.section@ashrae.org.

ASHRAE, 180 Technology Parkway NW, Peachtree Corners, GA 30092

(This foreword is not part of this standard. It is merely informative and does not contain requirements necessary for conformance to the standard. It has not been processed according to the ANSI requirements for a standard and may contain material that has not been subject to public review or a consensus process. Unresolved objectors on informative material are not offered the right to appeal at ASHRAE or ANSI.)

# FOREWORD

This addendum clarifies the definitions of WCF and WCFF.

Note: This addendum makes proposed changes to the current standard. These changes are indicated in the text by underlining (for additions) and strikethrough (for deletions) except where the reviewer instructions specifically describe some other means of showing the changes. Only these changes to the current standard are open for review and comment at this time. Additional material is provided for context only and is not open for comment except as it relates to the proposed changes.

Addendum o to Standard 34-2024

Add 6.1.5.2.1 and 6.1.5.2.2. The remainder of Section 6 remains unchanged.

6.1.5.2 Flammability Classification. Blends shall be assigned a flammability classification based on

the requirements in Section 6.1.3.

6.1.5.2.1 WCF

The highest concentration of flammable components with respect to LFL is that which provides the lowest LFL value. The most flammable composition with respect to burning velocity is that which provides the highest burning velocity value for the blend. First the WCF is determined based on the composition with lowest LFL as noted in section 6.1.3. If the applicant wants to apply for 2L classification, the burning velocity will be determined based on section 6.1.3.

6.1.5.2.2 WCFF

The highest concentration of flammable components with respect to LFL is that which provides the lowest LFL value. The most flammable composition with respect to burning velocity is that which provides the highest burning velocity value for the blend. Priority is given to determining the WCFF for the composition with lowest LFL first, after which the classification of 2L may be given based on the composition that gives the highest burning velocity per the requirements of section 6.1.3.

See informative appendix.

Add new Informative Appendix K as shown.

(This appendix is not part of this standard. It is merely informative and does not contain requirements necessary for conformance to the standard. It has not been processed according to the ANSI requirements for a standard and may contain material that has not been subject to public review or a consensus process. Unresolved objectors on informative material are not offered the right to appeal at ASHRAE or ANSI.)

INFORMATIVE APPENDIX K

EXAMPLE OF WCF SELECTION FOR BV AND LFL

Example

Here is an example of how to apply this wording by looking at a proposed R-32/1234yf (50/50 wt%) blend with tolerance of +/- 2 wt% for both components.

Determine WCF LFL based on each refrigerant LFL value (vol%), per ASHRAE table 4.1

- R-32 has an LFL of 14.4 vol%.

- R-1234yf has an LFL of 6.5 vol%.

| Refrigerant | LFL | Nominal | Range | WCFLFL based on Most Flammable composition |
| --- | --- | --- | --- | --- |
| R-32 | 14.4 vol% | 50 | 48-52 | 48 |
| R-1234yf | 6.5 vol% | 50 | 48-52 | 52 |

Determine WCF BV based on refrigerant lowest BV value (cm/s), per ASHRAE table 4.1

- R-32 has a BV of 6.7 cm/s.

- R-1234yf has a BV of 1.5 cm/s.

| Refrigerant | BV | Nominal | Range | WCFBV based on highest BV composition |
| --- | --- | --- | --- | --- |
| R-32 | 6.7 cm/s | 50 | 48-52 | 52 |
| R-1234yf | 1.5 cm/s | 50 | 48-52 | 48 |